## Slide 1: POWER TRANSMISSION & SWITCHYARD

## Slide 2
SAMPLE POWER TRANSMISSION DIAGRAM

## Slide 3: Power Flow Diagram
Stage-II (2X500MW)
5 Nos. Station Transformers
765 KV Switch Yard
IBT-1,2 &3
200MVA each
400 KV Switch Yard
132 KV Switch Yard
Stage-I (3x660MW)
ICT-1, 1000 MVA
ICT-2, 1000 MVA
2Nos.MUW PH
Ranchi-2nos.
Raipur-2nos
NTPC-Korba
Raipur-3
BILASPUR
3 nos

## Slide 4: HIGHLIGHTS
First switchyard charged at 765kV level.
Charged on 20th Jan 2007 by Hon MOP Shri. Sushil Kumar Shinde.
765kV Seoni line length – 357KM.(charged on 22nd Sep’07)
Power carrying capacity of each line – 2000MW.
ICT rating ( 765 / 400kV) – 1000 MVA
IBT(400/132 KV)-200 MVA
Number of breaks in a pole – FOUR.
Switchyard shield wire height – 46mtr.

## Slide 5
BILASPUR # 1
BILASPUR # 2
UNIT # 3
(660MW)
UNIT # 4
(500MW)
UNIT # 5
(500MW)
UNIT # 2
(660MW)
UNIT # 1
(660MW)
SIPAT -765 KV SWITCHYARD
ICT # 2
ICT # 1
3X1 Phase,
333MVA,
765/400KV
CB
CB
CB
CB
CB
CB
CB
CS
CS
CS
CS
CS
BUS # IV
BUS # III
BUS # II
BUS # I
3X1 Phase,
80MVAR
BUS SECTION # I I
BUS SECTION # I
3X1 Phase,
80MVAR
Circuit Breaker
CT
LA
CVT
6
Bay No-
Isolator with E/s
5
21
22
23
CS
BILASPUR # 3

## Slide 6
765kV SWITCHYARD SLD

## Slide 7
132kV SYSTEM(Single Breaker Scheme)

## Slide 8
400kV SWITCHYARD SLD

## Slide 9
A CONSOLIDATE SINGLE LINE DIAGRAM FOR VARIOUS AC VOLTAGE LEVEL USED IN PLANT

## Slide 10
Why AC??
and not HVDC

## Slide 13: MAINTENANCE
Very High Elevations
  Equipment 14mtr.
  Bus 25mtr.
  Jack bus 36mtr.
  Shield wire 46mtr.
Very High Induction voltage.

## Slide 14: CIRCUIT BREAKER
Model – GL 318
Height – 15Mtr
Break – 4 per pole.
Dielectric medium – SF6
Operating mechanism – Spring

## Slide 15: CURRENT TRANSFORMER
Model – CTH 765, Live tank
Height- 14 Mtr
Ratio – 3000-2000-1000-500/1

## Slide 16: ISOLATORS
Model – SPOLT, Italy
Horizontal Semi-pantograph Type
Maintenance free

## Slide 18: Wave Trap

## Slide 19: Voltage Transformer

## Slide 20: Transformers & Reactors

## Slide 21: COMPARISON
 | 400kV | 765kV
Ground Clearance | 8 Mtrs | 14 Mtrs
Phase to phase | 7 Mtrs | 14 Mtrs
Main Bus Height | 8 Mtrs | 26 Mtrs
Equipment Height | 8 Mtrs | 15 Mtrs
Jack Bus Height | 16 Mtrs | 38 Mtrs
Shielding Wire Height | 24.5 Mtrs | 46 Mtrs
Highest System Voltage | 420 Kv RMS | 800 Kv RMS
Lightning impulse voltage | 1425 Kvp | 2100 Kvp
Switching Impulse voltage | 1050 Kvp | 1550 Kvp
Power frequency withstand for 1 min | 630 Kv RMS | 830 Kv RMS

## Slide 22: CONVENTIONAL CONTROL AND PROTECTION PHILOSOPHY IN NTPC
PROTECTION & RELAY PANELS
CONTROL PANELS
CONTROL ROOM
HARD-WIRED FIELD INPUTS FOR
CONTROL AND PROTECTION
FUNCTIONS
CLOSE / OPEN
COMMANDS
PROTECTION
TRIP
COMMANDS
BMK
BMK
HARD-WIRED LOGIC IS FORMED IN BMK, CONTROL, RELAY AND PROTECTION PANELS FOR CONTROL AND PROTECTION TRIP FUNCTIONS

## Slide 23: WHAT IS SUBSTATION AUTOMATION SYSTEM
Automation, in general, means use of intelligent electronic devices (IEDs) to optimize the management of capital assets and enhance operation and maintenance (O&M) efficiencies with minimal human intervention
In the context of switchyards, automation means use of IEDs for control, protection and other data acquisition functions

## Slide 24: WHY SUBSTATION AUTOMATION SYSTEM
Rapid development and deployment of IEDs in substations like-
  Protective relays
  Energy metering systems
  Equipment condition monitoring systems e.g. On line dissolved gas monitors, partial discharge monitors, battery monitors etc.

## Slide 25: WHY SUBSTATION AUTOMATION SYSTEM
ISLANDS OF AUTOMATION WITHIN SUBSTATION
PROTECTION
SCADA
DFR/SOE
METERING
EQUIPMENT
DIAGNOSTICS
SUBSTATION
PROTECTION
METERING
OPERATIONS

## Slide 26
THANK YOU